## Size
Component | Unit | Class1 | Total
Genset | kW | - | 181.6129
NG Boiler | kW | 244.9506 | 244.9506

## Cost
Cost item | Component | Scenario | Unit | Class1 | Total
Net Present Cost | System | - | MUSD | - | 5.8189
Investment Cost | Genset | - | MUSD | - | 0.036323
| NG Boiler | - | MUSD | 0.024495 | 0.024495
Fixed Cost | Genset | - | MUSD | - | 0.050701
| NG Boiler | - | MUSD | 0.0051288 | 0.0051288
Fuel cost | Genset | 1 | MUSD | - | 3.765
| Boiler | 1 | MUSD | 1.9372 | 1.9372
Electric lost load cost | System | 1 | MUSD | - | 0
Thermal lost load cost | System | 1 | MUSD | 0 | 0

## Indicators
|  | Electric | Thermal | Total
Total Primary Energy Supply | MWh | 159247.4889 | 41965.3483 | 201212.8372
Fossil Primary Energy Supply | % | - | - | 1
Renewable Primary Energy Supply | % | - | - | 0
Efficiency | % | 0.3 | 0.87879 | 0.42071
Levelized Cost of Energy | USD/kWh | - | - | 0.29547